## Drop-Down Lists (hidden)
Slope | SoilTexture7080 | SlopeShape | LandscapePosition | SoilTextureOSTP | RedoxIndicators | AtGradeUp | 3 | PipeDia | DispersalMedia | Laterals | OtherEstabType | OtherEstabUnit | WebSoil Survey Rating | Shoreland Classification | 0 | Trench Distribution | Bed Dristribution | Pipe Diameter | Distribution Media | Separation Distance
0 | Sand | Linear, Linear | Depression | clay | None | 4 | 4 | 1 | Rock | 1 | Airport, bus station, rail depot | add for each nonresident meal | Not Limited | Lake - General Development | Chamber | Gravity - Drop Box | Pressure | 1.5 | Rock | 36
1 | Coarse Sand | Linear, Concave | Back/ Side Slope | silty clay | S1 | 3.85 | 4.17 | 1.25 | Registered Product: | 2 | Assembly hall | alley | Slightly Limited | Lake- Recreational | Chamber Low Profile | Gravity - Other | Gravity | 2 | Chamber | 60
2 | Loamy Sand | Linear, Convex | Foot Slope | sandy clay | S2 | 3.7 | 4.35 | 1.5 |  | 3 | Bar or lounge (no meals) | auditorium seat | Moderately Limited | Lake - Natural Environment | Chamber High Capacity | Pressure |  | 3 | Chamber Low Profile | 18
3 | Loamy Coarse Sand | Convex, Linear | Plain | clay loam | S3 | 3.57 | 4.54 | 2 | FlowClass | 4 | Barber shop* | bed | Very Limited | None | EzFlow |  |  |  | Chamber High Capacity | 12
4 | Fine Sand | Convex, Convex | Manmade | silty clay loam | S4 | 3.45 | 4.76 | 3 | I | 5 | Beauty salon* | bed | Extremely Limited | River - Agricultural | Eljen GSF |  |  |  | EzFlow
5 | Very Fine Sand | Convex, Concave | Stream/Terrace | sandy clay loam | T1 | 3.33 | 5 | 4 | II | 6 | Industrial building* | parking space |  | River - Tributary |  |  |  |  | Eljen GSF
6 | Loamy Fine Sand | Concave, Convex | Shoulder | silt | T2 | 3.23 | 5.26 | 6 | III | 7 | Bowling alley | car space |  | River - Forested
7 | Loamy Very Fine Sand | Concave, Concave | Summit | silt loam | T3 | 3.12 | 5.56 |  | IV | 8 | Cabin, resort | car stall |  | River - Transition
8 | Sandy Loam | Concave, Linear | Toe Slope | loam | T4 | 3.03 | 5.88 | Slopedir |  | 9 | Cafeteria | chair |  | River - Remote
9 | Coarse Sandy Loam |  | StructureShape | coarse sandy loam | T5 | 2.94 | 6.25 | north | DistType | 10 | Camp, day without meals | child |  | River - Urban
10 | Loam | RedoxKind | Single grain | medium sandy loam | T6 | 2.86 | 6.67 | northeast | Gravity | 11 | Camp, day and night with meals | convenience store customer
11 | Fine Sandy Loam | None | Granular | fine sandy loam | S1, T2 | 2.78 | 7.14 | northwest | Pressure | 12 | Camp, day with meals | customer
12 | Very Fine Sandy Loam | Concentrations | Platy | very fine loamy sand | S1, T3 | 2.7 | 7.69 | south | Pressure (non-level) | 13 | Industrial building* | employee
13 | Silt Loam | Depletions | Blocky | coarse loamy sand | S1, T4 | 2.62 | 8.29 | southeast |  | 14 | Industrial building* | parking space
14 | Silt | Gleyed | Prismatic | medium loamy sand | S1, T5 | 2.55 | 8.915 | southwest | MoundAbsorptionRatio | 15 | Institutional meals | parking space
15 | Clay Loam | Concentrations, gleyed | Massive | fine loamy sand | S1, T6 | 2.48 | 9.565 | east | 1 | 16 | Labor camp | passenger
16 | Sandy Clay Loam | Depletions, gleyed |  | very fine sand | S2, T2 | 2.41 | 10.24 | west | 1.5 | 17 | Labor camp (semi permanent) | patient
17 | Silty Clay Loam | Concentrations, depletions, gleyed | StructureConsistence | coarse sand | S2, T3 | 2.35 | 10.94 |  | 1.6 | 18 | Laundromat | person
18 | Sandy Clay | Concentrations, depletions | Loose | medium sand | S2, T4 | 2.29 | 11.665 | Parent Material | 1.8 | 19 | Medical office* | campsite with sewer hook-up (per person)
19 | Silty Clay | StructureGrade | Friable | fine sand | S2, T5 | 2.23 | 12.415 | Alluvium | 2 | 20 | Mental health hospital* | practitioner
20 | Clay | Structureless | Firm | very fine sand | S2, T6 | 2.18 | 13.19 | Bedrock | 2.1 |  | Motel | resident
21 | Bedrock | Weak | Extremely Firm | very fine sandy loam | S3, T1 | 2.13 | 13.99 | Colluvium | 2.3 |  | Nursing home, other adult congregate living | restroom
22 | Organic | Moderate | Rigid | bedrock | S3, T2 | 2.08 | 14.815 | Cut/Fill | 2.4 |  | Office | seat
23 | Fill Soil | Strong |  | organic | S3, T3 | 2.03 | 15.665 | Lacustrine | 2.5 |  | Other public institution | seat (open 16 hours or less, single service articles)
24 | EndCenter |  | PerfDia | VolumePipe | S3, T4 | 1.98 | 16.54 | Loess | 2.6 |  | Park or swimming pool | seat (open 16 hours or less)
25 | End | SHLR | 1/8 | 0.045 | S3, T5 | 1.93 | 17.44 | Organic | 2.7 |  | Permanent mobile home | seat (open more than 16 hours)
26 | Center | 0.3 | 3/16 | 0.078 | S3, T6 |  |  | Outwash | 2.9 |  | Prison or jail | seat (open more than 16 hours, single service articles)
27 | DepthAlarm | 0.42 | 5/32 | 0.11 | S4, T1 | CLR | YN | Till | 5 |  | Public lavatory | service bay
28 | 2 | 0.45 | 7/32 | 0.17 | S4, T2 | 1 | Yes |  | 5.3 |  | Public shower | Service station* customer
29 | 3 | 0.5 | 1/4 | 0.38 | S4, T3 | 2 | No |  | 7 |  | Resort | shower taken
30 |  | 0.52 | EfflScreen | 0.661 | S4, T4 | 3 | NA | YN-Optional |  |  | Restaurant (carry out including caterers) | campsite with sewer hook-up (per site/space)
| Tank Size | 0.6 | 1/8 |  | S4, T5 | 4 |  | Yes | MediaDepth |  | Restaurant (does not include bar or lounge) | campsite without sewer hook-up, with central toilet or shower facility (per site)
Bedrooms | 500 | 0.65 | 1/16 | DistMedia | S4, T6 | 5 |  | No | 0.5 |  | Restaurant (drive‑ in) | campsite without sewer hook-up, with central toilet or shower facility, served by dump station (per site)
2 | 1000 | 0.68 |  | Drainfield rock |  | 6 |  | Optional | 0.75 |  | Restaurant (short order) | square foot
3 | 1250 | 0.78 | Reduction | Drainfield rock & pea gravel |  | 7 |  | Recommended | 1 |  | Retail resort store | station
4 | 1500 | 0.87 | 1 | Sand | STA | 8 |  | Filter only |  |  | Retail store | student
5 | 2000 | 1 | 0.45 | Other | Trench | 9 |  |  |  |  | Rooming house | toilet
6 | 2500 | 1.2 |  |  | At-Grade | 10 |  | Landscape Position | Version |  | School (boarding) | user
7 |  | 1.6 | DepthPipe | DistHeadLoss | Mound | 11 |  | Summit | v 9.9.2021 |  | School (no gym, no cafeteria, and no showers) | visitor
8 | PerfSpace |  | 0.33 | 6.5 | Pressurized Bed | 12 |  | Shoulder |  |  | School (with cafeteria, gym, and showers) | with food vendor space
9 | 2 |  | 0.5 | 7 | Drip | 13 |  | Back/Side Slope | CoarseFragments |  | School (with cafeteria, no gym and no showers)
10 | 2.5 | MinHead |  | 9 |  | 14 |  | Foot Slope | <35% |  | Shopping center
11 | 3 | 2.5 | MediaLoadRate | 10 |  | 15 |  | Toe Slope | 35-50% |  | Stadium
12 | 3.5 | 3.5 | 1.2 |  |  | 16 |  |  | >50% |  | Theater
| 4 | 5 | 1 | ValueChroma |  | 17 |  |  |  |  | Visitor center
| 4.5 |  | 1.6 | 2/1 |  | 18
| 5 |  |  | 2/2 |  | 19 |  |  | SandySoilOptions
| ObservationType | SizeMult |  | 2.5/0 |  | 20 |  |  | Pressure distribution |  | Treatment Level | Pump Tank Type
| Probe | 1 | Hue | 2.5/1 |  |  |  |  | 5 feet of separation |  | C | Dosing
| Auger | 1.5 | 10R | 2.5/2 | Manifold Connection |  |  |  | Serial distribution in 15% sections |  | B | Equalization
| Pit |  | 2.5YR | 2.5/3 | Center | [5 empty] | B2 | Recirculation
|  |  | 5YR | 3/1 | End |  |  |  | PumpTankDesc |  | A
| PumpType |  | 7.5YR | 3/2 |  |  |  |  | Demand to Pressure |  | A2
| Demand Dosing Soil Treatment |  | 10YR | 3/3 |  |  |  |  | Demand to Gravity
| Time Dosing Soil Treatment |  | 2.5Y | 3/4 |  |  |  |  | Time to Pressure |  | Type of Wastewater
| Time Dosing Treatment Unit |  | 5Y | 3/6 |  |  |  |  | Time to Gravity |  | Residential | Limiting Condition
| Demand Dosing Treatment Unit |  | GLEY | 4/1 |  |  |  |  | Time to Treatment |  | Commercial | Redoximorphic Features/Saturated Soils
|  |  | N | 4/2 |  |  |  |  | Equalization |  | High-Strength | Bed Rock (including soild with >50% course fragments
|  |  | None | 4/3 | [7 empty] | Flood Elevation
| PumpTankType |  |  | 4/4 | MPCA Type |  |  |  | Nutrients |  | Soil Treatment Area Type | Restricted percolation rates/high clay content soils
| Demand Dosing |  | VegType | 4/6 | Type I |  |  |  | Nitrogen |  | Trench | Depth of Observation
| Equalization/Time Dosing |  | Lawn | 4/8 | Type II |  |  |  | Phosphorus |  | Bed
|  |  | Grass | 5/1 | Type III |  |  |  | Nitrogen & Phosphorus |  | Mound
|  |  | Forest | 5/2 | Type IV | [5 empty] | At-Grade
|  |  | Ag. Land | 5/3 | Type V |  |  |  | Treatment Level |  | Drip
|  |  | Row Crops | 5/4 |  |  |  |  | A
|  |  | Alfalfa | 5/6 | Rock Below Pipe Inches |  |  |  | A-2 |  | Distribution Type | Distribution Media
|  |  |  | 5/8 | 6 |  |  |  | B |  | Gravity Distribution | Rock
|  |  |  | 6/1 | 7 |  |  |  | B-2 |  | Pressure Distribution-Level | EzFlow
|  |  |  | 6/2 | 8 |  |  |  | C |  | Pressure Distribution-Unlevel | Chamber
|  |  |  | 6/3 | 9 | [6 empty] | .
|  |  |  | 6/4 | 10 |  |  |  | Type of Wastewater |  | Gravity or Pressure | .
|  |  |  | 6/6 | 11 |  |  |  | Residential |  | Gravity | .
|  |  |  | 6/8 | 12 |  |  |  | Other Est. - At-Risk |  | Pressure
|  |  |  | 7/1 |  |  |  |  | Other Est. - HSW
|  |  |  | 7/2 | Buoancy Tanks |  |  |  | Other Est. - Resid.
|  |  |  | 7/3 | Septic
|  |  |  | 7/4 | Dosing
|  |  |  | 7/6 | Equalization
|  |  |  | 7/8 | Recirculation
|  |  |  | 8/1 | Holding Tank
|  |  |  | 8/2 | Septic/Dosing Combo
8/3
8/4
8/6
8/8

## Residential Construction (hidden)
St. Louis County, MN |  | PERMIT Residential Construction Application Subsurface Sewage Treatment System |  |  |  |  | Form 3000 Rev. 01-02-2024
This permit application form is used to apply for a Permit to Construct. Additional Information: www.stlouiscountymn.gov/septic.
PROPERTY IDENTIFICATION NUMBER (PIN) and SITE
Primary Pin | 0 |  |  |  | Associated PIN
PIN is found on your Property Tax Statement (E.g. 123-1234-12345), searching the County Land Explorer at https://gis.stlouiscountymn.gov/landexplorer/, or searching the Property Lookup at http://apps.stlouiscountymn.gov/auditor/parcelInfo2005Iframe/.
Site Address | 0 |  |  |  |  | City | 0 | Zip | 0
Check to request a 911 address number and sign.
Visit https://www.stlouiscountymn.gov/departments-a-z/sheriff/emergency/911-emergency#5143571-obtaining-a-911-address for addressing information.
APPLICANT (Property Owner)
Name | [6 empty] | Date
Address |  |  |  | City |  | State |  | Zip
Email |  |  |  | Phone |  |  | Phone
CONTACT (If Different than Applicant Above)
Name
Email |  |  |  | Phone |  |  | Phone
Applicant MAILING INFORMATION (If Different than Site Address)
US Mail | Address |  |  | City |  | State |  | Zip
Email | Email
REASON FOR APPLICATON
New SSTS |  | Point of Sale Requirment
Replacing the exsisting SSTS. Why?
SYSTEM TYPE (refer to design summary) and PERMIT FEES
Type I |  | Type II |  | Type III |  | Type IV |  | Type V
Non Shoreland $325 |  | Holding Tank $270 |  | System $365 |  | System $420 |  | System $525
Shoreland $565 |  | Privy/Outhouse $110 |  | Component Add/Replace $215 |  | Component Add/Replace $215 |  | Component Add/Replace $215
Component Add/Replace $215 |  | Floodplain-Shoreland $330
Component Add/Replace $215
SITE INFORMATION (Check all that apply)
Yes | No | Is the SSTS within 1,000 feet of a lake or 300 feet of a river? |  |  |  | Lake/River Name
Yes | No | Is the property used year-round?
Yes | No | Is the property part of a CIC (Common Interest Community)? If yes, include the Associated PIN on this Application.
Yes | No | Is this property serving multiple dwellings sharing a SSTS component?
Yes | No | Is this leased property?
If yes, you must obtain & attach the Lessor’s written authorization for this project.
Leased From |  | MN Power |  | St. Louis County |  |  | Municipal
|  | MN DNR |  | US Forest Service
Water Source INFORMATION (Check all that apply)
Water Source | Proposed Well |  | Exsisting Well |  | Hand Carried |  | Surface/Lake water
Municipal
Well Type | Drilled |  | Sandpoint |  | Dug | More than one well? |  | Yes | No
Well # |  | Well depth Feet |  |  | Case Depth Feet
St. Louis County, MN |  |  | Page 1 of 2 |  |  | INCOMPLETE APPLICATIONS WILL BE RETURNED
St. Louis County, MN |  | PERMIT Residential Construction Application Subsurface Sewage Treatment System |  |  |  |  | Form 3000 Rev. 01-02-2024
DESIGNER
Licensed Business Name
License # |  |  | Certification #
Designer’s Comments (To Onsite Wastewater Staff)
STRUCTURE
Building Type and Water Uses |  | # of Bedrooms | Plumbing | Basement Plumbing | Garbage Disposal | Clothes Washer | Dishwasher | Water Conditioning Unit | Furnace w/Humidifier
Check all that apply
Dwelling | Home, mobile home, hunting shack, cabin.
Multi-Family | Multiple units
Accessory Dwelling | Guest cottage, bunk house
Accessory Structure | Garage, pole building, shed, sauna, gazebo screen-house
Other
Continued |  |  | Other information to be considered for this application
Bathtub > 40 gal | Sewer Grinder Pump | Sesonal Use
AGREEMENT
By submitting this application, the entire contents of which are considered to be public data, I certify and agree that I am the owner or the authorized agent of the owner of the above property, and that all uses will conform to the provisions of St. Louis County. I further certify and agree that I will comply with all conditions imposed in connection with the approval of the application. Applicants may be required to submit additional property descriptions, property surveys, site plans, building plans and other information before the application is accepted or approved. Intentional or unintentional falsification of this application or any attachments thereto will make the application, any approval of the application and any resulting permit invalid. I authorize St. Louis County staff to inspect the property to review the application and for compliance inspections. Furthermore, by submitting this application, I release St. Louis County and its employees from any and all liability and claims for damages to person or property in any manner or form that may arise from the approval of the application or any related plans, the issuance of any resulting permit or the subsequent location, construction, alteration, repair, extension, operation or maintenance of the subject matter of the application.
CONTACT Planning and Zoning (Onsite Wastewater Division)
Duluth Office |  |  |  |  | Virginia Office
Government Services Center 320 W 2nd Street, Suite 301 Duluth, MN 55802 |  |  | Phone (218) 725-5200 Toll Free (800) 450-9777 www.stlouiscountymn.gov/septic |  | Government Services Center 201 South 3rd Avenue West Virginia, MN 55792 |  | Phone (218) 749-0625 Toll Free (800) 450-9777 www.stlouiscountymn.gov/septic
OFFICE USE ONLY
Amount Paid |  | Paid by |  | Cash |  | Check # |  | Permit #
Revenue Code |  | Received By |  | ☐ Mail ☐ IP |  | Date RIO
St. Louis County, MN |  |  | Page 2 of 2 |  |  | INCOMPLETE APPLICATIONS WILL BE RETURNED

## Design Summary
St. Louis County, MN |  | PERMIT SSTS Design Summary Subsurface Sewage Treatment System | [23 empty] | Form 3002 Rev. 01-02-2026
This form is used to complete a SSTS Design. Additional Information: www.stlouiscountymn.gov/septic
SITE INFORMATION
Site Address |  |  | 0 | [8 empty] | City |  |  |  | Zip |  |  |  |  | Parcel ID
DESIGNER
Name | [25 empty] | Date
Email | [13 empty] | Phone | [7 empty] | Phone
SYSTEM INFORMATION
MPCA Type | [16 empty] | Dwelling Classification
Well Casing Depth
# Bedrooms |  |  |  |  | # Water using devices | [7 empty] | Total Finished Sq ft | [8 empty] | Sq ft / Bedroom |  |  |  |  | 0
Design Flow |  |  |  |  | Water Meter | [7 empty] | Pressure Test | [8 empty] | Grinder or Disposal
CLR | 0 | SLR |  |  | 0 | [7 empty] | Limiting Soil Type | [8 empty] | Limiting Layer Depth (in) | [5 empty] | 0
SSTS Flow Description
TANK INFORMATION
Type (Septic, Pump, Holding etc.) |  |  |  | Size (gallons) |  |  |  | Status (New, Existing) |  |  |  | Material (Precast, Plastic) |  |  |  | Alarm (Yes, No) |  |  | Insulated (Yes, No) |  |  |  | Bedded (Yes, No) |  |  | Building Sewer (Gravity, Pressure, Both)
Gallons per inch of pump tank | [6 empty] | 0
Tank Installation & Pumping comments
DISTRIBUTION INFORMATION
|  | Gal/Min | [6 empty] | Ft Head |  |  |  |  | Pump Model
[6 empty] | Time Dose Panel | [13 empty] | Timer On | [5 empty] | Timer Off |  |  | 0
Max Dose | 0 |  |  | Min. Dose | [5 empty] | Drainback | [5 empty] | Dose + Drainback | [8 empty] | Float Tether (in)
Manifold | [14 empty] | Laterals
Location | 0 | [13 empty] | Number |  | 0 | [7 empty] | Length (ft)
Diameter (in) | [14 empty] | Diameter (in) |  |  |  | 0
Insulated | [14 empty] | Orifices
[15 empty] | Size (in) |  | 0 | [7 empty] | # Per lateral
[15 empty] | Spacing (ft) |  |  |  | 0 |  |  |  | Shields
St. Louis County, MN |  | PERMIT SSTS Design Summary Subsurface Sewage Treatment System | [23 empty] | Form 3002 Rev. 01-02-2026
DRAINFIELD INFORMATION
Trench
Number | [6 empty] | Width (ft) | [7 empty] | Length (ft) | [8 empty] | Media Type
Max Depth (in) | [6 empty] | Rock (in) | [7 empty] | Cover (in) | [8 empty] | Sand Liner (in)
Bed
Number | [6 empty] | Width (ft) | [7 empty] | Length (ft) | [8 empty] | Media Type
Max Depth (in) | [6 empty] | Rock (in) | [7 empty] | Cover (in) | [8 empty] | Sand Liner (in)
At-Grade
Width (ft) |  |  |  | Length (ft) | [5 empty] | Number |  |  |  |  | Up Berm (ft) | [8 empty] | Down Berm (ft)
Mound
Number | [6 empty] | Bed Width (ft) |  |  | 0 |  |  |  |  | Bed Length (ft) |  |  |  | 0 |  |  |  |  | Media Type
Sand (in) | 36 | to |  | 36 |  |  | Rock (in) |  |  | 10 |  |  |  |  | Cover (in) | [8 empty] | Total Width (ft) |  |  | 0
Up Berm (ft) |  | 0 |  |  |  |  | Down Berm (ft) |  |  | 0 |  |  |  |  | Sand (yd3) |  |  |  | 0 |  |  |  |  | Total Length (ft) |  |  | 0
Registered Treatment Product
Filter Class
Media Type
No. of Filters | [6 empty] | Rock Bed Dimensions (ft) | [7 empty] | x |  |  | Bed Media Depth (in)
Manufacturer
Registered Aerobic Treatment System
Type
Gallons/day |  |  |  | No. of Units | [6 empty] | Disinfection (yes or no) | [8 empty] | If yes, chermical or UV
Manufacturer
Designer Comments
I hereby certify that I have completed this work in accordance with all applicable ordinances, rules and laws.
(Designer) | [7 empty] | (Signature) | [13 empty] | (License #) |  |  |  |  | (Date)
CONTACT Planning and Zoning (Onsite Wastewater Division)
Duluth Office | [14 empty] | Virginia Office
Government Services Center 320 W 2nd Street, Suite 301 Duluth, MN 55802 | [6 empty] | Phone (218) 725-5200 Toll Free (800) 450-9777 www.stlouiscountymn.gov/septic | [7 empty] | Government Services Center 201 South 3rd Avenue West Virginia, MN 55792 | [8 empty] | Phone (218) 749-0625 Toll Free (800) 450-9777 www.stlouiscountymn.gov/septic
Type I
Type II
Type IIII
Type IV
Type V
I
II
III
IV
Residential
Commercial
Seasonal
Other
Gravity
Drop Box
Distribution Box
Pressure
ETM
ETM
Intermittent/Single Pass
Reciculating
Subsurface Flow
Other
Sand
Peat
Textile/Synthetic
Constructed Wetland
Suspended Growth
Fixed Film
Sequencing Batch
Other

## Soil Log 1
|  | OSTP Soil Observation Log |  |  |  |  | Project ID: |  | v 03.19.15
Site Address: | [5 empty] | Legal Description/ GPS:
Soil parent material(s): (Check all that apply)
Landscape Position: (check one) | [7 empty] | Slope shape
Vegetation |  |  |  | Soil survey map units |  |  | Slope% |  | Elevation:
Weather Conditions/Time of Day: | [7 empty] | Date |  |  | 0
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
I hereby certify that I have completed this work in accordance with all applicable ordinances, rules and laws.
(Designer/Inspector) |  |  |  | (Signature) |  |  |  | (License #) |  | (Date)
Additional Soil Observation Logs | [6 empty] | Project ID: | #REF!
Client/ Address: | [5 empty] | Legal Description/ GPS:
Soil parent material(s): (Check all that apply)
Landscape Position: (check one) | [7 empty] | Slope shape
Vegetation |  |  |  | Soil survey map units |  |  | Slope% |  | Elevation:
Weather Conditions/Time of Day: | [7 empty] | Date
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
Textures: |  | Subsoil Indicator(s) of Saturation: |  |  |  |  | Consistence:
c-clay |  | S1. Distinct gray or red redox features |  |  |  |  | Loose- | Intact specimen not available
sic-silty clay |  | S2. Depleted matrix (value >/=4 and chroma </=2) |  |  |  |  | Friable- | Slight force between fingers
sc-sandy clay |  | S3. 5Y chroma </= 3 |  |  |  |  | Firm- | Moderate force between fingers
cl-clay loam |  | S4. 7.5 YR or redder faint redox concentrations or redox depletions |  |  |  |  | Extremely firm- | Moderate force between hands or slight foot pressure
sicl-silty clay loam |  |  |  | If yes to one of the above indicators then: |  |  | Rigid- | Foot pressure
scl-sandy clay loam |  |  |  | Topsoil Indicator(s) of Saturation: |  |  | Slope Shape:
si-silt |  |  |  | T1. Wetland Vegetation |  |  | Slope shape is described in two directions: up and down slope (perpendicular to the contour), and across slope (along the horizontal contour); e.g. Linear, Convex or LV'.
sil-silt loam |  | *Sand Modifiers |  | T2. Depressional Landscape
l-loam |  | co-coarse |  | T3. Organic texture or organic modifiers
sl-sandy loam* |  | m-medium |  | T4. N 2.5/ 0 color
ls-loamy sand* |  | f-fine |  | T5. Redox features in topsoil
s-sand* |  | vf-very fine |  | T6. Hydraulic indicators
Soil Structure
Grade:
Massive- | No observable aggregates, or no orderly arrangement of natural lines of weakness
Weak- | Poorly formed, indistinct peds, barely observable in place
Moderate- | Well formed, distinct peds, moderately durable and evident, but not distinct in undisturbed soil
Strong- | Durable peds that are quite evident in un-displaced soil, adhere weakly to one another, withstand displacement, and become separated when soil is disturbed
Loose- | No peds, sandy soil
Soil Structure
Shape:
Granular- | The peds are approximately spherical or polyhedral and are commonly found in topsoil. These are the small, rounded peds that hang onto roots when soil is turned over.
Platy- | The peds are flat and plate like. They are oriented horizontally and are usually overlapping. Platy structure is commonly found in forested areas just below the leaf litter or shallow topsoil.
Blocky- | The peds are block-like or polyhedral, and are bounded by flat or slightly rounded surface that are casting of the faces of surrounding peds. Blocky structure is commonly found in the lower topsoil and subsoil.
Prismatic- | Flat or slightly rounded vertical faces bound the individual peds. Peds are distinctly longer vertically, and faces are typically cast or molds of adjoining peds. Prismatic structure is commonly found in the lower subsoil.
Single Grain- | The structure found in a sandy soil. The individual particles are not held together.
Outwash
Lacustrine
Loess
Till
Alluvium
Bedrock
Organic Matter
Summit
Shoulder
Back/Side Slope
Foot Slope
Toe Slope
Outwash
Lacustrine
Loess
Till
Alluvium
Bedrock
Organic Matter
Summit
Shoulder
Back/Side Slope
Foot Slope
Toe Slope

## Soil log 2
|  | OSTP Soil Observation Log |  |  |  |  | Project ID: |  | v 03.19.15
Client/ Address: | [5 empty] | Legal Description/ GPS:
Soil parent material(s): (Check all that apply)
Landscape Position: (check one) | [7 empty] | Slope shape
Vegetation |  |  |  | Soil survey map units |  |  | Slope% |  | Elevation:
Weather Conditions/Time of Day: | [7 empty] | Date |  |  | 0
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
I hereby certify that I have completed this work in accordance with all applicable ordinances, rules and laws.
(Designer/Inspector) |  |  |  | (Signature) |  |  |  | (License #) |  | (Date)
Additional Soil Observation Logs | [6 empty] | Project ID: | #REF!
Client/ Address: | [5 empty] | Legal Description/ GPS:
Soil parent material(s): (Check all that apply)
Landscape Position: (check one) | [7 empty] | Slope shape
Vegetation |  |  |  | Soil survey map units |  |  | Slope% |  | Elevation:
Weather Conditions/Time of Day: | [7 empty] | Date
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
Observation #/Location: | [6 empty] | Observation Type:
Depth (in) | Texture | Rock Frag. % | Matrix Color(s) |  | Mottle Color(s) | Redox Kind(s) | Indicator(s) | I-------- Structure-----------I
[8 empty] | Shape | Grade | Consistence
Comments
Textures: |  | Subsoil Indicator(s) of Saturation: |  |  |  |  | Consistence:
c-clay |  | S1. Distinct gray or red redox features |  |  |  |  | Loose- | Intact specimen not available
sic-silty clay |  | S2. Depleted matrix (value >/=4 and chroma </=2) |  |  |  |  | Friable- | Slight force between fingers
sc-sandy clay |  | S3. 5Y chroma </= 3 |  |  |  |  | Firm- | Moderate force between fingers
cl-clay loam |  | S4. 7.5 YR or redder faint redox concentrations or redox depletions |  |  |  |  | Extremely firm- | Moderate force between hands or slight foot pressure
sicl-silty clay loam |  |  |  | If yes to one of the above indicators then: |  |  | Rigid- | Foot pressure
scl-sandy clay loam |  |  |  | Topsoil Indicator(s) of Saturation: |  |  | Slope Shape:
si-silt |  |  |  | T1. Wetland Vegetation |  |  | Slope shape is described in two directions: up and down slope (perpendicular to the contour), and across slope (along the horizontal contour); e.g. Linear, Convex or LV'.
sil-silt loam |  | *Sand Modifiers |  | T2. Depressional Landscape
l-loam |  | co-coarse |  | T3. Organic texture or organic modifiers
sl-sandy loam* |  | m-medium |  | T4. N 2.5/ 0 color
ls-loamy sand* |  | f-fine |  | T5. Redox features in topsoil
s-sand* |  | vf-very fine |  | T6. Hydraulic indicators
Soil Structure
Grade:
Massive- | No observable aggregates, or no orderly arrangement of natural lines of weakness
Weak- | Poorly formed, indistinct peds, barely observable in place
Moderate- | Well formed, distinct peds, moderately durable and evident, but not distinct in undisturbed soil
Strong- | Durable peds that are quite evident in un-displaced soil, adhere weakly to one another, withstand displacement, and become separated when soil is disturbed
Loose- | No peds, sandy soil
Soil Structure
Shape:
Granular- | The peds are approximately spherical or polyhedral and are commonly found in topsoil. These are the small, rounded peds that hang onto roots when soil is turned over.
Platy- | The peds are flat and plate like. They are oriented horizontally and are usually overlapping. Platy structure is commonly found in forested areas just below the leaf litter or shallow topsoil.
Blocky- | The peds are block-like or polyhedral, and are bounded by flat or slightly rounded surface that are casting of the faces of surrounding peds. Blocky structure is commonly found in the lower topsoil and subsoil.
Prismatic- | Flat or slightly rounded vertical faces bound the individual peds. Peds are distinctly longer vertically, and faces are typically cast or molds of adjoining peds. Prismatic structure is commonly found in the lower subsoil.
Single Grain- | The structure found in a sandy soil. The individual particles are not held together.
Outwash
Lacustrine
Loess
Till
Alluvium
Bedrock
Organic Matter
Summit
Shoulder
Back/Side Slope
Foot Slope
Toe Slope
Outwash
Lacustrine
Loess
Till
Alluvium
Bedrock
Organic Matter
Summit
Shoulder
Back/Side Slope
Foot Slope
Toe Slope

## Mound Calculations
| TYPE III time dosed Mound Calculations | [5 empty] | Updated: | 2023-05-01
Adjusted for Ordinance 61
Site address: |  | 0
A. SITE CONDITIONS
Evaluate the site and soils report for the following:
>Type and occupancy of facility.
>Quality of wastewater distributed.
>Dimensions and configuration of suitable on site area.
| >Treatment and hydraulic limitation of the soil |  |  | City
>Surface water movement.
(Note: shaded boxes to be filled in by designer)
| Slope | 0 | %
| Occupancy: One or two family dwelling |  |  |  | # of bedrooms = |  |  | Integer only
| Public facility (i.e. non-residential). Daily wastewater flow: | [6 empty] | gpd
(Provide details on flow estimate on separate sheet)
| Wastewater: Typical residential BOD5 |  |  |  | Y/N =
|  | Or other BOD5 = |  |  | mg/L
Soil limiting factor = |  |  |  | Depth to limiting factor = |  |  |  | inches
| Contour loading rate = |  |  | gpd / linear foot |  | Soil Loading Rate:
| Mound rock bed length= |  |  | ft | Soil Treatment Area (STA) flow= |  |  | 0
STA Flow (GPD)=Contour loading rate x rock bed length
| Berm Slope = |  |  | to | 1
B. DESIGN OF THE DISTRIBUTION CELL (ROCK BED)
Mound width not to exceed 10ft
A= | Mound rock bed width (ft)=
B= | Mound rock bed length (ft)=
1. Size of the Distribution Cell
a. Infiltration rate of fill material = |  |  |  |  | 1 | ( generally < 1.0 gal/sf/day)
b. Bottom area of distribution cell = Design wastewater flow divided by infiltration rate
(1.0 gal/sf/day)
Area = | 0 | sq. ft. | divided by | 1 | gal/sf/day | 0 | sq. ft.
C. SAND FILL DESIGN
1. Fill depth
a. Fill depth below distribution cell (at least 6 inches)
| 1) Minimum depth at up slope edge of distribution cell (D) = | [5 empty] | 36 | inches
(minimum 36 inches for treatment and 12 inches for dispersal) minus distance
in inches to limiting factor.
| Required separation distance |  |  |  | 36 | (36 inches or 12 inches minimum)
|  | minus | 0 | inches to saturated soil depth (from soils worksheet) =
| sand depth requirement |  |  | D = | 36 | inches
2) Depth at down slope edge of distribution cell (E)
E = depth at up slope edge of distribution cell (D) + ( % natural slope expressed
as a decimal x distribution cell width (A)
E = D + (% natural slope expresses as a decimal x A)
| E = |  | 36 | Inches + ( | 0 | x | 0 | feet x 12
inches/foot)
|  | E = | 36 | inches
b. Distribution Cell Depth of Aggregate (Rock Bed Depth)
Distribution cell depth (F) for aggregate distribution cell = amount of aggregate
below distribution laterals (6 inches min.) + nominal outside diameter of largest
lateral + amount of aggregate over distribution laterals (2 inches min.)
|  | F = | 6 | 6" min. + | 2 | inches + | 2 | (>2)inches
|  | F= | 10 | inches
Aggregate under laterals: minimum 6 inches to 12 inches
c. Cover Material
| 1) Depth at distribution cell center (H) > |  |  |  |  | 13 | inches (crown)
| 2) Depth at distribution cell edges (G) = |  |  |  |  | 12 | inches
2. Mound Dimensions, fill length and width
a. End berm width (K) = Total fill at center of distribution cell x horizontal gradient of
side slope.
K={([(D+E)divided by 2]+F+H)xhorizontal gradient of side slope}divided by 12inches/foot
| K = | 36 | + | 23 | x | 0 | divided by | 12
| K = | 0 | feet
b. Mound Length (L) = Distribution cell length + (2 x end berm width)
| L = | B + 2K
| L = | 0 | feet + 2 x | 0 | feet
| L = | 0
c. Up slope berm width (J) = Fill depth at upslope edge of distribution cell (D + F + G)
x horizontal gradient of side slope x slope correction factor
{100/[100 + (gradient of side slope x % of slope)]}
| J = ( | 36 | inches + | 10 | Inches + | 12 | inches) divided by
| 12 | inches/ft x | 0 | x | 100 | divided by [ | 100 | +
| ( | 0 | x | 0 | )
| J = | 0 | feet
d. Down slope berm width (I) = Fill depth at downslope edge of distribution cell
(E + F + G) x Horizontal gradient of side slope x downslope correction factor
100/[100 - (gradient of side slope x % of slope)]
I = (E + F + G) x Horizontal gradient of side slope x downslope correction factor
100 divided by [100 - (gradient of side slope x % of slope)]
| I = | 36 | inches + | 10 | Inches + | 12 | Inches) divided by
12in/ft x |  | 0 | x 100 divided by [100 -( |  | 0 | x | 0 | )]
| I = | 0 | feet
e. Mound width (W) = Up slope width (J) + Distribution cell width (A) + Downslope
width (I)
W = J + A + I
| W = | 0 | ft + | 0 | ft + | 0 | ft
| W = | 0 | feet
3. Determine the location of observation pipes along the length of distribution cell.
Distance from end of distribution cell to end observation pipes = B divided by 6
|  | Distance = |  | 0 | ft from ends of distribution cell.
D. SAND VOLUME CALCULATIONS
1. Estimated Sand = [sand beneath rock bed]+ [sand in downhill berm] + [sand in uphill berm]
+ [sand in end berms] x (1cubic yard/27 cubic feet)
2. Estimated Sand = (D + E ÷ 12 x B x A ÷ 2) + (E+12 ÷ 12 x L x I ) +
(D ÷ 12 x J x L ÷ 2) + (D ÷ 12 x A x K) ÷ 27
3. Estimated Sand = |  |  | 0 | cubic yards
4. Adjusted Sand Volume = Estimated sand x correction factor.
5. Adjusted Sand Volume = |  |  | 0 | x1.25 = | 0 | cubic yards
MOUND ABSORPTION
Mound Absorption Ratio = Mound Design Loading Rate ÷ Soil Loading Rate
|  |  | 1 | ÷ | 0 | = | #DIV/0!
Mound Absorption Width = (bed width or contour loading rate) x Mound Absorption Ratio
|  |  | 0 | X | #DIV/0! | = | #DIV/0! | Feet
| <1% Slope absoprtion length on both sides of bed width = |  |  |  |  | #DIV/0! | Feet
| >1% Slope absorption length on downslope = |  |  |  | #DIV/0! | Feet
Estimated Rock Volume= |  |  | 0 | x1.3 | 0 | CubicYards
Estimated Topsoil Volume= |  |  | 0 | x1.3 | 0 | Cubic Yards
0
0
0
0
10
36
0
0
36
0
1.0
:
6

## Pres. Dist.
Pressure Distribution Design Worksheet
[7 empty] | Project ID: |  | #REF! | [5 empty] | v 9.9.2021
1. | Media Bed Width: | [6 empty] | 0 |  | ft
2. | Minimum Number of Laterals in system/zone = Rounded up number of [(Media Bed Width - 4) ÷ 3] + 1.
|  | [( | 0 |  | - 4 ) ÷ 3] + 1 = |  |  | -0.33333 |  | laterals |  | Does not apply to at-grades
3. | Designer Selected Number of Laterals: | [8 empty] | laterals
Cannot be less than line 2 (Except in at-grades)
4. | Select Perforation Spacing: | [8 empty] | ft
5. | Select Perforation Diameter Size: | [8 empty] | in |  | FALSE
6. | Length of Laterals = Media Bed Length - 2 Feet.
| 0 | - | 2ft | = |  |  | ft | Perforation can not be closer then 1 foot from edge.
7. | Determine the Number of Perforation Spaces. Divide the Length of Laterals by the Perforation Spacing and round down to the nearest whole number.
| Number of Perforation Spaces= | [5 empty] | ft | ÷ |  |  | ft | = |  | Spaces
8. | Number of Perforations per Lateral is equal to 1.0 plus the Number of Perforation Spaces. Check table below to verify the number of perforations per lateral guarantees less than a 10% discharge variation. The value is double with a center manifold.
| Perforations Per Lateral = | [6 empty] | Spaces + 1 = |  |  |  |  | Perfs. Per Lateral
9. | Total Number of Perforations equals the Number of Perforations per Lateral multiplied by the Number of Perforated Laterals.
|  | Perf. Per Lat. X |  |  |  |  | Number of Perf. Lat. = | [5 empty] | Total Number of Perf.
10. | Spacing of laterals; Must be greater than 1 foot and no more than 3.5 feet: | [12 empty] | ft
11. | Select Type of Manifold Connection (End or Center):
12. | Select Lateral Diameter (See Table): | [9 empty] | in
13. | Calculate the Square Feet per Perforation.
Recommended value is 4-11 ft2 per perforation, Does not apply to At-Grades
a. | Bed Area = Bed Width (ft) X Bed Length (ft)
| 0 | ft X | 0 |  | ft = |  |  | ft2
b. | Square Foot per Perforation = Bed Area ÷ by the Total Number of Perfs
|  | ft2 ÷ |  |  | perf = |  |  | ft2/perf
14. | Select Minimum Average Head: | [9 empty] | ft
15. | Select Perforation Discharge based on Table: | [8 empty] | GPM per Perf
16. | Flow Rate = Total Number of Perfs X Perforation Discharge.
|  | Perfs X |  |  |  | GPM per Perforation = | [5 empty] | GPM
17. | Volume of Liquid Per Foot of Distribution Piping (Table II): | [10 empty] | Gallons/ft
18. | Volume of Distribution Piping =
= [Number of Perforated Laterals X Length of Laterals X (Volume of Liquid Per Foot of Distribution Piping]
|  | X |  |  | ft X |  |  | gal/ft = |  |  |  | Gallons
19. | Minimum Delivered Volume = Volume of Distribution Piping X 4
|  | gals X 4 = |  |  |  |  | Gallons
Comments/Special Design Considerations:

## Pump-Basic(1)
Basic Pump Selection Design Worksheet
1. | PUMP CAPACITY | [5 empty] | Project ID: |  | #REF! | [7 empty] | v 9.9.2021
| Pumping to Gravity or Pressure Distribution: | [5 empty] | Pressure | [9 empty] | 0
A. | If pumping to gravity enter the gallon per minute of the pump: | [9 empty] | GPM | (10 - 45 gpm)
B. | If pumping to a pressurized distribution system: | [7 empty] | 0 |  | GPM
C. | Enter pump description: | [7 empty] | Equalization/Time Dosing
City
2. HEAD REQUIREMENTS
A. | Elevation Difference |  |  |  |  | ft
between pump and point of discharge:
B. | Distribution Head Loss: |  |  |  |  | ft
C. | Additional Head Loss: |  |  |  |  | ft (due to special equipment, etc.)
D. | 1. Supply Pipe Diameter: |  |  |  |  | in
| 2. Supply Pipe Length: |  |  |  |  | ft
E. | Friction Loss in Plastic Pipe per 100ft from Table I:
| Friction Loss = |  |  |  | ft per 100ft of pipe
F. | Determine Equivalent Pipe Length from pump discharge to soil dispersal area discharge point. Estimate by adding 25% to supply pipe length for fitting loss. Supply Pipe Length X 1.25 = Equivalent Pipe Length
|  | ft | X | 1.25 | = |  |  | ft
G. | Calculate Supply Friction Loss by multiplying Friction Loss Per 100ft by the Equivalent Pipe Length and divide by 100.
Supply Friction Loss =
|  | ft per 100ft |  |  | X |  |  | ft | ÷ | 100 | = |  |  | ft
H. | Total Head requirement is the sum of the Elevation Difference + Distribution Head Loss, + Additional Head Loss + Supply Friction Loss
|  | ft | + |  |  | ft | + |  |  | ft + |  |  | ft = |  |  | ft
3. PUMP SELECTION
A pump must be selected to deliver at least | [7 empty] | GPM with at least | [6 empty] | feet of total head.
Comments:
[18 empty] | Fitting Type | 1.5 | 2 | 3
[18 empty] | Gate Valve | 1.07 | 1.38 | 2.04
[18 empty] | 90 Deg Elbow | 4.03 | 5.17 | 7.67
[18 empty] | 45 Deg Elbow | 2.15 | 2.76 | 4.09
[18 empty] | Tee - Flow Thru | 2.68 | 3.45 | 5.11
[18 empty] | Tee - Branch Flow | 8.05 | 10.3 | 15.3
[18 empty] | Swing Check Valve | 13.4 | 17.2 | 25.5
[18 empty] | Angle Valve | 20.1 | 25.8 | 38.4
[18 empty] | Globe Valve | 45.6 | 58.6 | 86.9
[18 empty] | Butterfly Valve | x | 7.75 | 11.5

## Pump-Tank(Other)Time
NON STA Pump Tank Design Worksheet (Time Dose) | [20 empty] | To use these calculations you must unprotect the worksheet under the Review Tab.
[11 empty] | Project ID: | [7 empty] | v 03.15.2023 |  | MEASURED TANK CAPACITY (existing tanks):
DETERMINE TANK CAPACITY AND DIMENSIONS
1. | A. | STA Flow | [5 empty] | 0 |  | GPD | B. | Tank Use: | [7 empty] | A. | Rectangle area = Length (L) X Width (W)
| C. | Percentage of Design Flow |  |  |  |  | % | 0 |  | Gal | Up to 75% design flow is normal for Design percentage | [10 empty] | 3.14 X |  |  |  | 2 | ft | = |  | ft2
| D. | Min. required pump tank capacity: | [7 empty] | Gal | E. | Recommended capacity: | [5 empty] | Gal |  | C. | Calculate Gallons Per Inch. Multiply the area from 1.A or 1.B, by 7.5 to determine the gallons per foot the tank holds and divide by 12 to calculate the gallons per inch.
2. | A. | Tank Manufacturer: | [8 empty] | B. | Tank Model: | [10 empty] | ft2 | X | 7.5 gal/ft3 ÷ 12 in/ft |  |  |  | = |  | Gallons per inch
| C. | Capacity from manufacturer: | [7 empty] | Gallons |  |  | Note: Design calculations are based on this specific tank. Substituting a different tank model will change the pump float or timer settings. Contact designer if changes are necessary. | [6 empty] | D. | Calculate Total Tank Volume
| D. | Gallons per inch: | [7 empty] | Gallons per inch | [10 empty] | Depth from bottom of inlet pipe to tank bottom: | [9 empty] | in
| E. | Liquid depth of tank from manufacturer: | [7 empty] | inches | [10 empty] | Total Tank Volume = Depth from bottom of inlet pipe (Line 4.A) X Gallons/Inch (Line 2)
DETERMINE DOSING VOLUME | [22 empty] | in | X | 0 |  | Gallons Per Inch = |  |  |  | Gallons
3. | Volume to Cover Pump (The inlet of pump should be 4 in from the bottom of the tank & 2 in covering the pump recommended)
(Pump and block height + 2 inches) X Gallons Per Inch
| ( |  |  | in + | 2 inches) X |  |  |  | Gallons Per Inch |  | = |  |  | Gallons
4. | Minimum Delivered Volume: Based on use of second pump tank
[12 empty] | Gallons (minimum dose) | [5 empty] | inches/dose
5. | Calculate Maximum Pumpout Volume (25% of Design Flow)
| Design Flow: |  |  | 0 |  | GPD | X | 0.25 | = | 0 |  | Gallons (maximum dose) | [5 empty] | inches/dose
6. | Select a pumpout volume that meets both Minimum and Maximum: | [11 empty] | Gallons
7. | Calculate Doses Per Day = Percentage Design Flow ÷ Delivered Volume
|  | 0 |  | gpd ÷ |  |  |  | gal = |  |  |  | Doses
8. | Calculate Drainback:
| A. | Diameter of Supply Pipe= | [6 empty] | 0 |  | inches
| B. | Length of Supply Pipe = | [6 empty] | 0 |  | feet
| C. | Volume of Liquid Per Lineal Foot of Pipe = | [8 empty] | Gallons/ft
| D. | Drainback = Length of Supply Pipe X Volume of Liquid Per Lineal Foot of Pipe
|  | 0 |  | ft X |  |  | gal/ft = |  |  |  | Gallons
9. | Total Dosing Volume = Delivered Volume plus Drainback
|  |  |  | gal + |  |  | gal = |  |  | Gallons
10. | Working Storage Volume = Tank Volume -Volume to Cover Pump - Reserve Capacity
| 0 |  | gal - |  |  | gal - | #VALUE! |  | = | #VALUE! |  | Gallons
11. | Required Flow Rate:
A. | From Pump Curve - Must verify after Install: | [8 empty] | GPM* | [5 empty] | *Note: This value must be adjusted after installation based on pump calibration.
B. | Calculated (measured) GPM = Change in Depth (in) x Gallons Per Inch / Time Interval in Minutes
|  |  |  | in X |  |  |  | gal/in ÷ |  |  |  | min = |  |  | GPM
12. | Select Flow Rate from Line 11.A or 11.B: | [7 empty] | GPM*
NORMAL OPERATION TIMER SETTINGS*
13. | Calculate TIMER ON setting*:
| Total Dosing Volume ÷ GPM | [11 empty] | HR | MIN | SEC
|  |  | gal | ÷ |  |  | gpm = |  |  |  | Minutes ON* |  | #VALUE! | #VALUE! | #VALUE!
14. | Calculated TIMER OFF setting*:
| Minutes Per Day (1440)/Doses Per Day - Minutes On | [14 empty] | HR | MIN | SEC
| 1440 min ÷ |  |  | doses/day - |  |  |  |  | min | = |  |  | Minutes OFF* |  |  | #VALUE! | #VALUE! | #VALUE!
OPTIONAL PEAK ENABLE DOSING* - Designer's option for peak flow operation
15. | Peak Percentage of Design Flow | [6 empty] | %
16. | Peak Pump out Volume that meets both Minimum and Maximum Volume | [11 empty] | gal + | Drainback |  |  |  | gal
17. | Peak Dose Volume |  |  |  |  | gal | [8 empty] | HR | MIN | SEC
18. | Peak TIMER ON |  |  |  |  | gal ÷ |  | gpm = |  |  | min ON
| *Note: This value must be adjusted after installation based on pump calibration. | [13 empty] | HR | MIN | SEC
19. | Peak TIMER OFF:1440 min ÷ |  |  |  |  | doses/day - |  |  | min On |  |  |  | min Off
FLOAT SETTINGS |  |  |  | Alarm and Pump are to be wired on separate circuits and inspected by the electrical inspector
20. | Pump Off Float - Measuring from bottom of tank:
Distance to set Pump Off Float=Gallons to Cover Pump / Gallons Per Inch:
|  |  | gal ÷ |  |  |  | gal/in = |  |  |  | inches |  | Reserve Capacity |  |  |  | #VALUE! | Gal
[12 empty] | Alarm Depth |  |  | in
21. | Alarm Float - Measuring from bottom of tank (90% recommended): | [10 empty] | Storage Capacity |  |  |  |  | #VALUE! | Gal
| Distance to set Alarm Float = Tank Depth X % of Tank Depth (90% recommended) | [11 empty] | Normal Dose Volume |  |  |  |  | Gal
|  |  | in X |  |  |  | % = |  |  |  | inches
[12 empty] | Pump Off |  |  | in |  |  | Gal
22. | Reserve Capacity in gallons = (Tank Depth - Alarm Depth) X GPI
( | 0 |  | in - |  |  |  | in) X |  |  |  | = | #VALUE! |  | gallons
Width
Length
Radius

## Tank Buoyancy
Tank Buoyancy Worksheet
1. Tank Specifications | [6 empty] | Project ID: |  | #REF! | [6 empty] | v 9.9.2021
A. | Tank Manufacturer: | [9 empty] | Tank Model:
B. | Outside Tank Dimensions and Specifications: | [9 empty] | Tank Use:
| Length: |  | in | Width: |  | in | Height: |  | in | Diameter: |  |  | in
| Length: |  | ft | Width: |  | ft | Height: |  | ft | Radius of Tank: |  |  | in
City
2. Outside Volume of Tank
Rectangular Tank | [9 empty] | Circular Tank
A. | Area of Tank = Length (ft) X Width (ft) | [8 empty] | A. | Area of Tank = πr2 (3.14 X (Radius of Tank)2)
|  |  | ft X |  |  | ft = |  |  | ft2 |  | 3.14 X |  |  | ft2 = |  | ft2
B. | Volume of Tank = Area of Tank (2.A) X Height (ft) | [8 empty] | B. | Volume of Tank = Area of Tank X Height (ft)
|  |  | ft X |  |  | ft = |  |  | ft3 |  |  | ft2 X |  |  | ft = |  | ft3
3. Force of Tank Weight (FTW)
| Weight of Tank (provided by manufacturer) | [7 empty] | lbs/ft3
4. Force of Soil Weight Over Tank (FSW)
[11 empty] | Soil Type | Weight of Soil (lbs/ft3)
A. | Depth of Cover Over Tank: |  |  |  |  | in |  | ft
B. | Weight of Soil Per Cubic Foot: | [6 empty] | lbs/ft3 |  |  | Sandy | 120
C. | Volume of Soil Over Tank = Depth of Cover (ft) X Area of Tank (ft2) | [9 empty] | Loamy | 100
|  | ft X |  |  | ft2 = |  |  | ft3 |  |  | Clay | 90
D. | Weight of Soil Over Tank = Volume of Soil Over Tank X Weight of Soil Per Cubic Foot
|  | ft3 X |  | lbs/ft3 = |  |  | lbs | Note: Assumes saturation does not get over the lid of the tank
5.Buoyant Force (FB)
Buoyant Force (FB) = Outside Volume of Tank X Weight of Water Per Cubic Foot (62.4 lbs/ft3) X 1.2 (Safety Fctr)
|  |  | X 62.4 lbs/ft3 X 1.2 = | [5 empty] | lbs
6. Evaluation of Net Forces
A. | Downward Force = Force of Tank Weight (FTW) + Force of Soil Weight of Soil (FSW)
|  |  | lbs + |  |  | lbs = |  |  | lbs
B. | Net Difference = Downward Force - Buoyant Force Including Safety Factor
|  |  | lbs - |  |  | lbs = |  |  | lbs
If the Net Difference is negative, countermeasures will need to be taken to prevent the tank from floating out of the ground.
Comments/Solution: