| St. Louis County, MN |  |  | PERMIT SSTS Dwelling Classification Worksheet Subsurface Sewage Treatment System |  |  |  |  |  |  |  |  |  |  |  | Form 3011 Rev. 12-28-2021 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| This form is used to complete a SSTS Design. Additional Information: www.stlouiscountymn.gov/septic |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # SITE INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Address |  |  |  |  |  |  |  | City |  |  |  |  | Zip | Parcel ID |  |
| # DWELLING INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dwelling dimensions (ft) |  |  |  |  | x |  | Finished Square Feet |  |  |  |  |  |  |  |  |
| Number of Bedrooms |  |  |  |  |  |  | Finished Square Feet per Bedroom |  |  |  |  |  |  |  |  |
| Information provided by |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # WATER USING DEVICES (check all that apply) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ | Clothes Washing Machine |  |  |  |  |  |  |  | ☐ |  | Bathtub > 40 gallons |  |  |  |  |
| ☐ | Dishwasher |  |  |  |  |  |  |  | ☐ |  | Garbage Disposal |  |  |  |  |
| ☐ | Water Conditioning Unit |  |  |  |  |  |  |  | ☐ |  | Self-cleaning Humidifier in Furnace |  |  |  |  |
| # CLASSIFICATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ I |  | More than 800 finished square feet per bedroom and/or more than 2 water using devices |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ II |  | Between 500 and 800 finished square feet per bedroom and not more than 2 water using devices |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ III |  | Less than 500 finished square feet per bedroom and not more than 2 water using devices |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ☐ IV |  | Dwellings with wastewater systems designed under part 7080.2240 |  |  |  |  |  |  |  |  |  |  |  |  |  |

# Extracted from SLC Ordinance 61 Technical Standards

# 7080.1860 DESIGN FLOW (GALLONS PER DAY).

TABLE IV

Classification of dwelling

|  | I** | II | III |  |  | IV |
| --- | --- | --- | --- | --- | --- | --- |
| Number of bedrooms | Gallons per day |  |  |  |  |  |
| 2 or less | 300 | 225 | 180 |  |  | * |
| 3 | 450 | 300 | 218 |  |  | * |
| 4 | 600 | 375 | 256 |  |  | * |
| 5 | 750 | 450 | 294 |  |  | * |
| 6 | 900 | 525 | 332 |  |  | * |

* Flows for Classification IV dwellings are 75 percent of the values as determined for Classification I, II, or III systems.

** Design flows for Class I dwellings wastewater systems with design flows at a minimum 100 gallons per day per bedroom

must meet the requirements of 7080.2300, Item I.

For more than six bedrooms, the design flow is determined by the following formulas:

Classification I: Classification I dwellings are those with more than 800 square feet per bedroom, when the dwelling's total finished floor area is divided by the number of bedrooms, or where more than two of the following water-use appliances are installed or anticipated: clothes washing machine, dishwasher, water conditioning unit, bathtub greater than 40 gallons, garbage disposal, or self-cleaning humidifier in furnace. The design flow for Classification I dwellings is determined by multiplying 150 gallons by the

number of bedrooms.

Classification II: Classification II dwellings are those with 500 to 800 square feet per bedroom, when the dwelling's total finished floor area is divided by the number of bedrooms, and where no more than two of the water-use appliances listed in Classification I are installed or anticipated. The design flow for Classification II dwellings is determined by adding one to the number of bedrooms and multiplying this result by 75 gallons.

Classification III: Classification III dwellings are those with less than 500 square feet per bedroom, when the dwelling's total finished floor area is divided by the number of bedrooms, and where no more than two of the water-use appliances listed in Classification I are installed or anticipated. The design flow for Classification III dwellings is determined by adding one to the number of bedrooms, multiplying this result by 38 gallons, then adding 66 gallons.

Classification IV: Classification IV dwellings are dwellings with wastewater systems designed under part 7080.2240.